## Applicant details
ID | Owner of the data centre | Operator of the data centre | Name and location
| Article 5.16b 2b | Article 5.16b 2a | Article 5.16b 2b | Article 5.16b 2b
referentie ID | name owner | name operator | data centre name | LAU Code
Staatsblad 2024, 122; Article 5.16b (officielebekendmakingen.nl)
More information: | COMMISSION DELEGATED REGULATION (EU) of 14.3.2024 on the first phase of the establishment of a common Union rating scheme for data centres
Annexes to the Delegated Act on the first phase of the establishment of a common Union rating scheme for data centres
Note on A4: Choose your own reference.
Note on D4: ‘data centre operator’ means enterprise data centre operator, colocation data centre operator or co-hosting data centre operator;
Note on G4: In The Netherlands the LAU Code format consists of 'GM' followed by three digits. See: https://ec.europa.eu/eurostat/web/nuts/local-administrative-units

## Datacenter details
ID | Data centre details
| Annex XVD 3.1 | Article 5.16b 2c |  | Annex XVD 3.2.1 | Annex XVD 3.2.1 | Annex XVD 3.2.1 | Annex XVD 3.2.2 | Annex XVD 3.2.2
referentie ID | type of data centre | operational Start Year | operational Start Month | electric Infra Redundancy At High Voltage Level | electric Infra Redundancy At Low Voltage Level | electric Infra Redundancy At Rack Level | cooling Infra Redundancy At Room Level | cooling Infra Redundancy At Rack Level
Data whose secrecy is justified under article 5.1(1)(c) 'Wet open overheid', is exempt from the obligation according to article 1 and 2. Leave the corresponding questions empty.
Wet open overheid (rvo.nl)
| ENTERPRISE_DATA_CENTRE_STRUCTURE |  | JANUARY
| COLLOCATION_DATA_CENTRE_STRUCTURE |  | FEBRUARY
| CO-HOSTING_DATA_CENTRE_STRUCTURE |  | MARCH
| ENTERPRISE_DATA_CENTRE_GROUP_OF_STRUCTURES |  | APRIL
| COLLOCATION_DATA_CENTRE_GROUP_OF_STRUCTURES |  | MAY
| CO-HOSTING_DATA_CENTRE_GROUP_OF_STRUCTURES |  | JUNE
JULY
SEPTEMBER
OCTOBER
NOVEMBER
DECEMBER
Note on B4: 1) ‘enterprise data centre’ means a data centre that is operated by an enterprise, and of which the sole purpose is to deliver and manage the information technology needs of the enterprise; 2) ‘colocation data centre’ means a data centre in which one or more customers install and manage their own network or networks, servers and storage equipment and services; 3) ‘co-hosting data centre’ means a data centre in which one or more customers are provided with access to network or networks, servers, and storage equipment on which they operate their own services and applications and where both the information technology equipment and the support infrastructure of the building are provided as a service by the data centre operator.
Note on C4: the calendar year during which the reporting data centre started providing information technology services.
Note on D4: the calendar month during which the reporting data centre started providing information technology services.
Note on E4: electrical infrastructure redundancy level at high voltage level; For the redundancy levels, if "N" represents the baseline number of components or functions to satisfy the normal conditions, redundancy shall be expressed compared to that baseline "N", for example as "N+1," "N+2," "2N", etc.
Note on F4: electrical infrastructure redundancy level at low voltage level; For the redundancy levels, if "N" represents the baseline number of components or functions to satisfy the normal conditions, redundancy shall be expressed compared to that baseline "N", for example as "N+1," "N+2," "2N", etc.
Note on G4: electrical infrastructure redundancy level at rack level; For the redundancy levels, if "N" represents the baseline number of components or functions to satisfy the normal conditions, redundancy shall be expressed compared to that baseline "N", for example as "N+1," "N+2," "2N", etc.
Note on H4: cooling infrastructure redundancy level at room level; For the redundancy levels, if "N" represents the baseline number of components or functions to satisfy the normal conditions, redundancy shall be expressed compared to that baseline "N", for example as "N+1," "N+2," "2N", etc.
Note on I4: cooling infrastructure redundancy level at rack level; For the redundancy levels, if "N" represents the baseline number of components or functions to satisfy the normal conditions, redundancy shall be expressed compared to that baseline "N", for example as "N+1," "N+2," "2N", etc.

## Power demand; Floor area
ID | it Power Demand Installed |  | total Floor Area |  | total Computer Room Floor Area
| Annex XVD 1 |  | Annex XVD 2.1 |  | Annex XVD 2.2
referentie ID | value | unit | value | unit | value | unit
|  | KW |  | M2 |  | M2
|  | KW |  | M2 |  | M2
|  | KW |  | M2 |  | M2
|  | KW |  | M2 |  | M2
|  | KW |  | M2 |  | M2
|  | KW |  | M2 |  | M2
|  | KW |  | M2 |  | M2
|  | KW |  | M2 |  | M2
|  | KW |  | M2 |  | M2
|  | KW |  | M2 |  | M2
Data whose secrecy is justified under article 5.1(1)(c) 'Wet open overheid', is exempt from the obligation according to article 1 and 2. Leave the corresponding questions empty.
Wet open overheid (rvo.nl)
Note on B2: the sum of the nominal power demand, in kW, of the network or networks, servers and storage equipment installed in the data centre computer room floor area.
Note on D2: the total floor area of all floors of the structure or group of structures that constitute the data centre.
Note on F2: the total floor area within the data centre that accommodates the data processing, data storage and telecommunication equipment that provide the information technology services of the data centre;

## Energy consumption; Water input
ID | total Energy Consumption |  | EDC from backup generators |  | total Energy Consumption IT Equipment |  | electrical Grid Functions | average Battery Capacity |  | total Water input |  | total Potable Water Input
| Annex XVD 4.1 |  | Annex XVD 4.1 |  | Annex XVD 4.2 |  | Annex XVD 4.3 | Annex XVD 4.4 |  | Annex XVD 5 |  | Annex XVD 5
referentie ID | value | unit | value | unit | value | unit | text | value | unit | value | unit | value | unit
|  | KWH |  | KWH |  | KWH |  |  | KW |  | M3 |  | M3
|  | KWH |  | KWH |  | KWH |  |  | KW |  | M3 |  | M3
|  | KWH |  | KWH |  | KWH |  |  | KW |  | M3 |  | M3
|  | KWH |  | KWH |  | KWH |  |  | KW |  | M3 |  | M3
|  | KWH |  | KWH |  | KWH |  |  | KW |  | M3 |  | M3
|  | KWH |  | KWH |  | KWH |  |  | KW |  | M3 |  | M3
|  | KWH |  | KWH |  | KWH |  |  | KW |  | M3 |  | M3
|  | KWH |  | KWH |  | KWH |  |  | KW |  | M3 |  | M3
|  | KWH |  | KWH |  | KWH |  |  | KW |  | M3 |  | M3
|  | KWH |  | KWH |  | KWH |  |  | KW |  | M3 |  | M3
Data whose secrecy is justified under article 5.1(1)(c) 'Wet open overheid', is exempt from the obligation according to article 1 and 2. Leave the corresponding questions empty.
Wet open overheid (rvo.nl)
Note on B2: Total energy consumption includes the use of electricity, fuels and other energy sources used for cooling. The amount of EDC coming from backup generators (EDC-BG, in kWh) shall be measured separately.
Note on D2: Total energy consumption includes the use of electricity, fuels and other energy sources used for cooling. The amount of EDC coming from backup generators (EDC-BG, in kWh) shall be measured separately.
Note on F2: the sum of the nominal power demand, in kW, of the network or networks, servers and storage equipment installed in the data centre computer room floor area; Where the installed information technology power demand has changed during the reporting period, a weighted average shall be used. Where the installed information technology power demand cannot be determined, the data centre rated information technology power demand (in kW), as defined in Article 2, can be used. Where the data centre rated information technology power
Note on H2: the information on whether any functions that support the stability, reliability, and resilience of the electrical grid are provided by the data centre, such as peak demand shifting or firm frequency response (FFR);
Note on I2: the average capacity of the data centre batteries that were offered to the grid via a relevant market or contracts for electrical grid functions;
Note on K2: total Water usage of the datacentre
Note on M2: total potable water usage of the datacentre.

## Waste heat
ID | waste Heat Reused |  | average Waste Heat Temperature |  | Average Intake Air Temperature |  | refrigerant Type | cooling Degree Days
| Annex XVD 6.1 |  | Annex XVD 6.2 |  | Annex XVD 7 |  | Annex XVD 6.3 | Annex XVD 6.4
referentie ID | value | unit | value | unit | value | unit | refrigerantType | value | unit
|  | KWH |  | CELSIUS_DEGREE |  | CELSIUS_DEGREE |  |  | DEGREE_DAY
|  | KWH |  | CELSIUS_DEGREE |  | CELSIUS_DEGREE |  |  | DEGREE_DAY
|  | KWH |  | CELSIUS_DEGREE |  | CELSIUS_DEGREE |  |  | DEGREE_DAY
|  | KWH |  | CELSIUS_DEGREE |  | CELSIUS_DEGREE |  |  | DEGREE_DAY
|  | KWH |  | CELSIUS_DEGREE |  | CELSIUS_DEGREE |  |  | DEGREE_DAY
|  | KWH |  | CELSIUS_DEGREE |  | CELSIUS_DEGREE |  |  | DEGREE_DAY
|  | KWH |  | CELSIUS_DEGREE |  | CELSIUS_DEGREE |  |  | DEGREE_DAY
|  | KWH |  | CELSIUS_DEGREE |  | CELSIUS_DEGREE |  |  | DEGREE_DAY
|  | KWH |  | CELSIUS_DEGREE |  | CELSIUS_DEGREE |  |  | DEGREE_DAY
|  | KWH |  | CELSIUS_DEGREE |  | CELSIUS_DEGREE |  |  | DEGREE_DAY
Data whose secrecy is justified under article 5.1(1)(c) 'Wet open overheid', is exempt from the obligation according to article 1 and 2. Leave the corresponding questions empty.
Wet open overheid (rvo.nl)
Note on B2: Data centres shall measure the heat that is used or reused outside of the data centre boundary, and which substitutes partly or totally energy needed outside the data centre boundary.
Note on D2: measured as the temperature of the fluid used to cool the information and communication technology equipment in the data centre computer room, averaged over the year, and across every measurement point.
Note on F2: measured as the average setpoint temperature in all data centre computer rooms, set as a setpoint command to the cooling system used for the information and communication technology equipment in the data centre computer rooms averaged over the year.
Note on H2: Volgens Regulation (EU) No 517/2014
Note on I2: determined as the number of cooling degree days for the location of the reporting data centre during the last calendar year, by using the methodology used by Eurostat and the Joint Research Centre or equivalent, and with a base temperature of 21 degree Celsius. Open access sources shall be used to determine the cooling degree days;

## Renewable energy
ID | total Renewable Energy Consumption |  | total Renewable Energy Consumption GoO |  | total Renewable Energy Consumption PPA |  | total Renewable Energy Consumption OS
| Annex XVD 8 |  | Annex XVD 8a |  | Annex XVD 8b |  | Annex XVD 8c
referentie ID | value | unit | value | unit | value | unit | value | unit
|  | KWH |  | KWH |  | KWH |  | KWH
|  | KWH |  | KWH |  | KWH |  | KWH
|  | KWH |  | KWH |  | KWH |  | KWH
|  | KWH |  | KWH |  | KWH |  | KWH
|  | KWH |  | KWH |  | KWH |  | KWH
|  | KWH |  | KWH |  | KWH |  | KWH
|  | KWH |  | KWH |  | KWH |  | KWH
|  | KWH |  | KWH |  | KWH |  | KWH
|  | KWH |  | KWH |  | KWH |  | KWH
|  | KWH |  | KWH |  | KWH |  | KWH
Data whose secrecy is justified under article 5.1(1)(c) 'Wet open overheid', is exempt from the obligation according to article 1 and 2. Leave the corresponding questions empty.
Wet open overheid (rvo.nl)
Note on B2: ERES-TOT is the sum of ERES-GOO, ERES-PPA and ERES-OS
Note on D2: determined as the sum of the Guarantees of Origin purchased and retired by the reporting data centre. The data centre shall measure the ERES-PPA that enters the data centre boundary, and which cannot be counted for more than one data centre or be created from power purchasing agreements or on-site renewables;
Note on F2: determined as the amount of energy from Power Purchasing Agreements made by the reporting data centre. The data centre shall measure the ERES-PPA that enters the data centre boundary, and which cannot be counted for more than one data centre.
Note on H2: measured as the energy generated from on-site renewable energy sources within the data centre boundary.

## Capacity; Bandwidth
ID | ict Servers Capacity |  | ict Storage Capacity |  | incoming Bandwidth |  | outgoing Bandwidth |  | incoming Data |  | outgoing Data
| Annex XVD 9.1 |  | Annex XVD 9.2 |  | Annex XVD 10.1 |  | Annex XVD 10.2 |  | Annex XVD 10.3 |  | Annex XVD 10.4
referentie ID | value | unit | value | unit | value | unit | value | unit | value | unit | value | unit
Data whose secrecy is justified under article 5.1(1)(c) 'Wet open overheid', is exempt from the obligation according to article 1 and 2. Leave the corresponding questions empty.
Wet open overheid (rvo.nl)
Note on B2: the sum of the SERT active state performance or equivalent for all servers. Server ICT capacity is the active state performance rating as declared in the manufacturer information in accordance with Commission Regulation (EU) 2019/424.
Note on D2: the storage capacity in petabytes, namely the sum of the raw (addressable) capacity of all SSD and HDD storage devices installed in all the storage equipment as declared by the storage device manufacturer.
Note on F2: measured in gigabytes per second as the total provisioned bandwidth for incoming traffic to the data centre computer room, aggregated for all the connectivity capacity, and averaged over the year; Gigabyte per second (GB/s or GBps) is a unit of data transfer rate equal to 8 gigabits per second.
Note on H2: measured in gigabytes per second as the total provisioned bandwidth for outgoing traffic from the data centre computer room, aggregated for all the connectivity capacity, and averaged over the year; Gigabyte per second (GB/s or GBps) is a unit of data transfer rate equal to 8 gigabits per second.
Note on J2: measured in exabytes as the total incoming data to the data centre computer room, aggregated over the course of the reporting year, irrespective of the number of the data centre’s connections;
Note on L2: measured in exabytes as the total outgoing data from the data centre computer room, aggregated over the course of the reporting year, irrespective of the number of the data centre’s connections.
Note on C4: Use the drop down menu to choose the right unit
Note on E4: Use the drop down menu to choose the right unit
Note on G4: Use the drop down menu to choose the right unit
Note on I4: Use the drop down menu to choose the right unit
Note on K4: Use the drop down menu to choose the right unit
Note on M4: Use the drop down menu to choose the right unit